Gate Valve 
for BAIO®plus System, tension proof,
PN 16
DN 80...300
Socket connection on both sides,
Body parts made of ductile iron EN-JS 1030 (GGG-40),
with double-function socket on both sides
for positive direct interior interlocking 
with BAIO®plus System parts and for
exterior interlocking of plastic pipes,
socket designed for sealing ring to DIN 28 603,
with inserted TYTON sealing rings for cast-iron pipes,
or with inserted GKS sealing rings for plastic pipes (PVC and PE),
continuous pipe culvert,
boltless cover,
with inside screw,
wedge vulcanized all over with EPDM, with wedge drainage,
stem made of stainless steel with min. 13 % Cr,
maintenance-free stem seal,
(O-rings inserted in brass bushing)
Corrosion protection: 	inside and outside
			epoxy coating,
			blue, RAL 5005,
			according to GSK 

e.g. 	VAG BETA® 200 Gate Valve socket/socket 
for cast-iron or plastic pipes,
or similar

Options:	- with VAG VA telescopic equipment
	Adjustment range:	1.00 - 1.40 m
				1.20 - 1.80 m
				1.70 - 2.70 m
                  - with enclosed position indicator

Pc ........   Euro/Pc .........   Euro/Item .........