Gate Valve 
for BAIO®plus System, tension proof,
PN 16
DN 80...300
Spigot end /Socket connection,
Body parts made of ductile iron EN-JS 1030 (GGG-40),
with double-function socket and spigot end
for positive direct interior interlocking 
with BAIO®plus System parts and for
exterior interlocking of plastic pipes,
socket designed for sealing ring to DIN 28 603,
with inserted TYTON sealing ring for cast-iron pipes,
or with inserted GKS sealing ring for plastic pipes (PVC and PE)
continuous pipe culvert,
boltless cover,
with inside screw,
wedge vulcanized all over with EPDM, with wedge drainage,
stem made of stainless steel with min. 13 % Cr,
maintenance-free stem seal,
(O-rings inserted in brass bushing)
Corrosion protection: 	inside and outside
			epoxy coating,
			blue, RAL 5005,
			according to GSK 

e.g. 	VAG BETA® 200 Gate Valve socket/spigot 
for cast-iron or plastic pipes
or similar

Options:	- with VAG VA telescopic equipment
	Adjustment range:	1.00 - 1.40 m
				1.20 - 1.80 m
				1.70 - 2.70 m
                  - with enclosed position indicator
	
Pc.......   Euro/Pc .........   Euro/Item .........