Underground Hydrant with double sealing system
DN 80, DIN 3221, 
type AD
with a safety locking system for internal parts, 
with additional automatic float ball shut-off
with automatic drainage and protection against loss of supply water, 
body parts of ductile iron, 
stem of stainless steel, min. 13% Cr. 
stem sealed with rubber 0-rings in brass bush, maintenance free 
screws and thrust pipe of stainless steel, 
stem nut and seat bush of brass, 
main valve of ductile iron, fully covered with rubber (EPDM)
flange dimension to EN 1092, PN 16
Corrosion protection:	inside: true enamel, 
outside: epoxy coating 
blue, RAL 5005

		alternative: inside and outside epoxy coating

Cover depth: 0,75m

On request
- cover depth	1,00 m
- cover depth	1,25 m
- cover depth	1,50 m

e.g.	VAG SUPRA 280 V Underground Hydrant
	with Double Sealing System 

Pcs. ......... Euro/pcs .........    Euro/item.........